Advertisement iso685W-S-B + FP200W

Isolation Monitoring Device according to DIN EN 61557-8 for monitoring AC-, DC- and AC/DC IT-Systems according to DIN VDE 0100-410:2007-06 with the possibility for mounting in frontpanels.

iso685W-S-B + FP200W, Art.-Nr.:B91067220W

Nominal voltage: AC 0 ... 690 V; 0.1 Hz... 460 Hz; DC 0 ... 1000 V
Measuring range: 0,1 kΩ ... 20 MΩ
Response values: adjustable 1 kΩ ... 10 MΩ
Uncertainty (response values): ±15 %, minimum ±1 kΩ

Rated supply voltage: AC/DC 24...240 V; DC, 47...460 HZ

Dimensions (L x B x H):
-iso685W-S-B: 108 mm x 96 mm x 110 mm
-FP200W: 134 mm x 72 mm x 35,6 mm

Operating temperature: -40...70° C

Degree of protection, installations: IP 40
Degree of protection, clamps: IP 20

User Interface:
-Backlighted LC-Display 40 mm x 40 mm with 127 x 127 Pixel
-Display FP200W is integrable in front panel opening 66 mm x 138 mm
-Discharged or on the rear side of iso685W-S-B on FP200W mountable
-LED’s for Service, Operating, Alarm 1, Alarm 2

Interface: 
-Integrated Webserver
-Modbus TCP Communication
-BCOM Interface over Ethernet
-1 Buzzer
-2 separated adjustable potential-free changeover contacts (NC, NO selectable)
-2 separate adjustable digital outputs.
-3 of 10 functions can be dedicated to each output / relay / buzzer. The functions have an OR-linkage.
-3 separate adjustable digital inputs.
-1 of 4 functions can be dedicated to each input.
-1 analog output (0...20 mA, 4...20 mA, 0...400µA, 0...10V, 2...10V)

Handling: 6 backlighted keys

Max. system leakage capacitance: 1000 µF

Measuring voltage: dependent on profile, ±10 V, ±50 V

Internal resistance: ≥ 124 kΩ

Measuring current: ≤ 403 µA

Additional measurand:
-Voltage measuring
-Frequency measuring
-Capacitance measuring

Connection:
-Screw termination
-Push in termination

Coupling Monitoring: 
-Permanent coupling monitoring of the measurement connections to the monitored system in life systems.
-Monitoring the connection to the earth.

Other: 
-Internal decoupling switches for use in coupled systems
- Predefined measurement profiles
- Adaption of measuring voltage depending on the profile

Accessories:
-Plug component kit screw termination* (B91067901)
-Plug component kit push in termination (B91067902)
-Mechanical Accessories* (termination coverage, 2 assembly clip (B91067903)
-FP200W* (B91067904W)
-Frontcover 144x72 transparent (for IP65) (B98060005)
*(included in delivery B91067220W)

Manufacturer:
Bender GmbH & Co. KG
Londorfer Straße 65
35305 Grünberg

Type: iso685W-S-B + FP200W
Part Number: B91067220W
Unit:  piece